Yes. For testing FMWorks properly, the seed work orders should not all be simple open corrective jobs. They should exercise different equipment, priorities, lifecycle states, assignments, dates, safety conditions, costs, vendors, overdue situations, and closure outcomes.

Below is a practical UAT dataset you can enter into FMWorks.

FMWorks Work Order UAT Test Dataset

Use these work orders to test the complete FMWorks workflow from creation through assignment, execution, verification and closure.

WO-TEST-001 — Emergency Chilled Water Pump Failure

Work Order No.: WO-TEST-001
Title: Chilled Water Pump P-CHW-01 Tripped
Work Type: Corrective Maintenance
Category: Mechanical
Priority: Critical / Emergency
Status: Open
Location: Utility Block – Chiller Plant Room
Asset: P-CHW-01 – Chilled Water Pump No. 1
Reported By: Operations Control Room
Assigned Department: Mechanical Maintenance
Assigned To: Mechanical Technician A
Date Reported: 27 Aug 2026
Target Completion: 27 Aug 2026
Estimated Duration: 3 hours
Estimated Cost: S$800

Problem Description:
Chilled water pump P-CHW-01 tripped during normal operation. Standby pump P-CHW-02 started automatically. Investigate the cause of trip and restore P-CHW-01 to service.

Safety Requirements:
LOTO required before electrical or mechanical inspection.

Work Instructions:
Check motor protection relay, MCC indication, pump coupling, bearing condition and motor current. Identify trip cause before resetting.

Expected UAT Scenario:
Tests emergency work order creation, Critical priority, immediate assignment and same-day completion.

WO-TEST-002 — AHU Preventive Maintenance

Work Order No.: WO-TEST-002
Title: Quarterly Preventive Maintenance – AHU-02
Work Type: Preventive Maintenance
Category: HVAC
Priority: Medium
Status: Scheduled
Location: Main Building – Level 2 AHU Room
Asset: AHU-02
Reported By: FMWorks Preventive Maintenance Schedule
Assigned Department: HVAC Maintenance
Assigned To: HVAC Technician A
Date Reported: 25 Aug 2026
Scheduled Date: 30 Aug 2026
Target Completion: 30 Aug 2026
Estimated Duration: 2 hours
Estimated Cost: S$150

Work Description:
Perform quarterly inspection and servicing of AHU-02.

Work Instructions:
Inspect filters, belts, bearings, cooling coil, drain pan, condensate drain, motor condition, vibration and operating temperature. Record supply and return air temperatures.

Expected UAT Scenario:
Tests planned preventive maintenance and future scheduling.

WO-TEST-003 — Electrical Distribution Board Hot Spot

Work Order No.: WO-TEST-003
Title: Investigate Abnormal Temperature at DB-L2-03
Work Type: Corrective Maintenance
Category: Electrical
Priority: High
Status: In Progress
Location: Main Building – Level 2 Electrical Room
Asset: DB-L2-03
Reported By: Electrical Technician
Assigned Department: Electrical Maintenance
Assigned To: Senior Electrical Technician
Date Reported: 26 Aug 2026
Target Completion: 28 Aug 2026
Estimated Duration: 4 hours
Estimated Cost: S$500

Problem Description:
Thermal inspection detected elevated temperature at the Phase B outgoing cable termination.

Safety Requirements:
Electrical isolation and LOTO required. Arc-flash PPE required.

Work Instructions:
Verify temperature with thermal camera, inspect termination, check torque and cable condition and perform corrective work after approved isolation.

Expected UAT Scenario:
Tests High priority, electrical safety controls and an In Progress work order.

WO-TEST-004 — Fire Alarm Detector Fault

Work Order No.: WO-TEST-004
Title: Smoke Detector SD-L1-024 Intermittent Fault
Work Type: Corrective Maintenance
Category: Fire Protection
Priority: High
Status: Pending Vendor
Location: Main Building – Level 1 Warehouse
Asset: SD-L1-024
Reported By: Security Control Room
Assigned Department: Facilities / Fire Protection
Assigned To: Fire Alarm Contractor
Vendor: ABC Fire Systems Pte Ltd
Date Reported: 24 Aug 2026
Target Completion: 28 Aug 2026
Estimated Cost: S$380

Problem Description:
Fire alarm panel intermittently reports detector communication fault. Detector resets but fault subsequently returns.

Work Instructions:
Vendor to inspect detector head, base, loop wiring and fire alarm panel event history.

Expected UAT Scenario:
Tests external vendor assignment and Pending Vendor status.

WO-TEST-005 — Water Leakage in Toilet

Work Order No.: WO-TEST-005
Title: Water Leakage Below Wash Basin
Work Type: Corrective Maintenance
Category: Plumbing
Priority: Low
Status: Open
Location: Main Building – Level 1 Male Toilet
Asset: PLB-L1-WB-03
Reported By: Building User
Assigned Department: Building Maintenance
Assigned To: Maintenance Technician B
Date Reported: 27 Aug 2026
Target Completion: 1 Sep 2026
Estimated Duration: 1 hour
Estimated Cost: S$50

Problem Description:
Small amount of water observed leaking from the waste connection below the wash basin.

Expected UAT Scenario:
Tests routine Low-priority maintenance.

WO-TEST-006 — Lift Breakdown

Work Order No.: WO-TEST-006
Title: Passenger Lift LIFT-01 Out of Service
Work Type: Breakdown
Category: Vertical Transportation
Priority: Critical
Status: Pending Vendor
Location: Main Building
Asset: LIFT-01
Reported By: Security
Assigned Department: Facilities Management
Assigned To: Lift Service Contractor
Vendor: XYZ Elevator Services Pte Ltd
Date Reported: 27 Aug 2026
Target Completion: 27 Aug 2026
Estimated Cost: S$1,200

Problem Description:
Passenger lift stopped at Level 2 and subsequently became unavailable. No passengers trapped.

Safety Requirements:
Lift to remain isolated and "Out of Service" signage displayed until vendor clearance.

Expected UAT Scenario:
Tests Critical vendor-dependent breakdown handling.

WO-TEST-007 — Solar PV Inverter Alarm

Work Order No.: WO-TEST-007
Title: Solar Inverter INV-PV-02 Communication Failure
Work Type: Corrective Maintenance
Category: Renewable Energy
Priority: Medium
Status: Open
Location: Utility Block – Solar Equipment Room
Asset: INV-PV-02
Reported By: BMS Operator
Assigned Department: Electrical Maintenance
Assigned To: Electrical Technician B
Date Reported: 26 Aug 2026
Target Completion: 31 Aug 2026
Estimated Duration: 2 hours
Estimated Cost: S$200

Problem Description:
BMS has lost communication with solar PV inverter INV-PV-02. Inverter local display remains operational.

Expected UAT Scenario:
Tests a non-critical controls/communications fault.

WO-TEST-008 — Generator Monthly Test

Work Order No.: WO-TEST-008
Title: Monthly Emergency Generator Functional Test
Work Type: Preventive Maintenance / Testing
Category: Electrical
Priority: Medium
Status: Completed
Location: Utility Block – Generator Room
Asset: GEN-01
Reported By: FMWorks Maintenance Schedule
Assigned Department: Electrical Maintenance
Assigned To: Electrical Technician A
Scheduled Date: 20 Aug 2026
Completed Date: 20 Aug 2026
Estimated Duration: 1.5 hours
Actual Duration: 1.4 hours
Estimated Cost: S$100
Actual Cost: S$95

Work Performed:
Generator started in manual and automatic modes. Battery voltage, oil pressure, coolant temperature, output voltage and frequency recorded. Automatic transfer sequence verified.

Completion Result: Passed.

Status: Completed

Expected UAT Scenario:
Tests successfully completed work with actual labour/cost information.

WO-TEST-009 — Overdue Exhaust Fan Repair

Work Order No.: WO-TEST-009
Title: Exhaust Fan EF-05 Excessive Vibration
Work Type: Corrective Maintenance
Category: Mechanical
Priority: Medium
Status: Open – Overdue
Location: Main Building – Roof
Asset: EF-05
Reported By: Maintenance Technician
Assigned Department: Mechanical Maintenance
Assigned To: Mechanical Technician B
Date Reported: 10 Aug 2026
Target Completion: 15 Aug 2026
Estimated Cost: S$450

Problem Description:
Excessive vibration and abnormal bearing noise detected during routine inspection.

Expected UAT Scenario:
Tests overdue calculations, dashboard alerts and escalation.

WO-TEST-010 — Transformer Oil Leak

Work Order No.: WO-TEST-010
Title: Minor Oil Seepage at Transformer TR-01
Work Type: Inspection / Corrective
Category: Electrical
Priority: High
Status: Awaiting Approval
Location: Utility Block – Transformer Yard
Asset: TR-01
Reported By: Electrical Engineer
Assigned Department: Electrical Maintenance
Date Reported: 27 Aug 2026
Target Completion: 3 Sep 2026
Estimated Cost: S$4,500

Problem Description:
Oil staining observed around transformer radiator flange. No significant reduction in transformer oil level detected.

Recommended Action:
Engage transformer specialist to inspect flange, gasket condition and determine whether shutdown is required.

Expected UAT Scenario:
Tests approval workflow before expensive maintenance.

WO-TEST-011 — Spare Part Unavailable

Work Order No.: WO-TEST-011
Title: Replace Failed Bearing – Cooling Tower Fan CT-02
Work Type: Corrective Maintenance
Category: Mechanical
Priority: High
Status: On Hold – Awaiting Parts
Location: Utility Block – Roof
Asset: CT-02-FAN
Reported By: Mechanical Technician
Assigned Department: Mechanical Maintenance
Assigned To: Mechanical Technician A
Date Reported: 22 Aug 2026
Target Completion: 5 Sep 2026
Estimated Cost: S$1,800

Problem Description:
Fan drive-end bearing has excessive noise and vibration. Replacement bearing is not currently available in store.

Parts Required:
1 × Fan drive-end bearing.

Expected UAT Scenario:
Tests parts dependency, inventory linkage and On Hold status.

WO-TEST-012 — Rejected Closure

Work Order No.: WO-TEST-012
Title: Repair Loading Bay Roller Shutter
Work Type: Corrective Maintenance
Category: Building / Architectural
Priority: Medium
Status: Reopened
Location: Main Building – Loading Bay
Asset: RS-01
Reported By: Warehouse Supervisor
Assigned Department: Building Maintenance
Assigned To: Maintenance Contractor
Date Reported: 18 Aug 2026
Original Completion: 23 Aug 2026
Estimated Cost: S$650

Problem Description:
Roller shutter intermittently jams approximately halfway during closing.

Previous Work:
Contractor adjusted shutter limit switches and submitted the work order as completed.

Verification Result:
Failed. Shutter jammed again during FM verification.

Closure Decision: Rejected.

Status: Reopened

Expected UAT Scenario:
Tests completion → verification failure → rejection → reopened workflow.

WO-TEST-013 — Safety Hazard

Work Order No.: WO-TEST-013
Title: Damaged Electrical Socket at Pantry
Work Type: Safety Corrective Maintenance
Category: Electrical
Priority: Critical
Status: In Progress
Location: Main Building – Level 2 Pantry
Asset: SOCKET-L2-P-04
Reported By: Staff Member
Assigned Department: Electrical Maintenance
Assigned To: Electrical Technician B
Date Reported: 27 Aug 2026
Target Completion: 27 Aug 2026
Estimated Cost: S$80

Problem Description:
Socket faceplate cracked with internal components potentially accessible.

Immediate Action:
Socket isolated and warning label installed.

Expected UAT Scenario:
Tests safety hazard reporting and immediate risk-control recording.

WO-TEST-014 — No Fault Found

Work Order No.: WO-TEST-014
Title: Investigate Reported FCU Abnormal Noise
Work Type: Inspection
Category: HVAC
Priority: Low
Status: Closed
Location: Main Building – Level 2 Office
Asset: FCU-L2-08
Reported By: Office User
Assigned Department: HVAC Maintenance
Assigned To: HVAC Technician B
Date Reported: 21 Aug 2026
Completed Date: 21 Aug 2026
Actual Duration: 0.5 hour
Actual Cost: S$30

Problem Description:
User reported intermittent abnormal noise from FCU.

Finding:
FCU inspected and operated through normal range. No abnormal noise, vibration or mechanical defect detected.

Resolution:
No fault found. User advised to report recurrence.

Closure Code: No Fault Found

Expected UAT Scenario:
Tests closure without repair or replacement.

WO-TEST-015 — Major Capital Repair

Work Order No.: WO-TEST-015
Title: Replace Main Chilled Water Pump Motor
Work Type: Major Corrective Maintenance
Category: Mechanical / Electrical
Priority: High
Status: Awaiting Management Approval
Location: Utility Block – Chiller Plant
Asset: P-CHW-03-MTR
Reported By: Facilities Engineer
Assigned Department: Engineering
Date Reported: 27 Aug 2026
Target Completion: 15 Sep 2026
Estimated Duration: 3 days
Estimated Cost: S$18,500

Problem Description:
Motor insulation resistance has deteriorated and winding condition assessment recommends motor replacement.

Proposed Work:
Supply replacement motor, remove existing motor, install replacement, perform alignment, insulation testing, rotation check and operational testing.

Approval Required: Yes – expenditure exceeds maintenance approval threshold.

Expected UAT Scenario:
Tests high-value approval and major maintenance workflow.

UAT Coverage

These 15 records should collectively test:

- Corrective maintenance

- Preventive maintenance

- Breakdown maintenance

- Inspection/testing

- Critical, High, Medium and Low priorities

- Open

- Scheduled

- In Progress

- Pending Vendor

- Awaiting Approval

- On Hold

- Completed

- Closed

- Reopened

- Overdue

- Internal technicians

- External contractors

- LOTO requirements

- Electrical safety

- Fire protection

- Mechanical systems

- HVAC

- Plumbing

- Building works

- Renewable energy

- Parts dependency

- Estimated versus actual cost

- Same-day emergency response

- Future scheduled work

- Overdue work

- Successful completion

- No-fault-found closure

- Failed verification/reopening

- High-value management approval

- Preventive-maintenance-generated work orders

One important recommendation: don't enter all 15 manually if FMWorks already has—or is about to have—an import function. This dataset is ideal for creating a CSV seed/import file and using it to test bulk work-order creation as well. That gives us two UAT tests at once: work-order functionality + CSV import functionality.

I would also add another 5 deliberately problematic records afterward—missing assignee, invalid target date, duplicate WO number, inactive asset, and invalid cost—to confirm FMWorks correctly rejects bad data rather than accepting everything.